EEN442 Laboratory Report

High Voltage, Protection and SCADA Systems

Erasmus lab week at Hochschule Darmstadt (h_da), 19 to 23 October 2026

Group report (2 students) · Experimental analysis

Submission Groups: 2 students per group. Both students are jointly responsible for the whole report. Where: Moodle (EEN442). One submission per group, uploaded by one group member. Deadline: Sunday 1 November 2026. Format: A single PDF file named EEN442_Lab_Surname1_Surname2.pdf. Page limits: Part 1: max. 3 pages. Part 2: max. 4 pages. Part 3: max. 2 pages. The limits include text, tables and plots. The cover information, Appendix A (photographs) and Appendix B (raw measurement tables) do not count. Figures and tables: Number and caption every figure and table, label all axes with quantity and unit, and use SI units. Plots should be generated from your measured data.

# Student Information

|  | Name | Student ID |
| --- | --- | --- |
| Student 1 |  |  |
| Student 2 |  |  |

| Date of submission |  |
| --- | --- |

# Part 1: High Voltage Laboratory. Breakdown Strength in Air

Maximum 3 pages

## 1.1 Experimental Setup Description

Describe the high voltage test setup used in your experiment, including all major components and their functions. Address the following points:

Main components of the AC test circuit: variable transformer (ST), 100 kV high voltage transformer (HS), 100 pF measuring capacitor (CM) and 50 kΩ series resistor (RV)

Modifications for the DC tests: rectifier diodes (GD), 10 000 pF DC capacitor (CS) and earthing switch with 416 Ω resistor (ES)

Safety systems and grounding equipment employed, and the safety briefing procedure

The measurement and control instruments used to acquire breakdown voltages (AC peak and DC measurement)

How the electrode configurations (plate-plate, point-plate, point-point) were assembled and the gap distance set

The voltage ramp-up procedure and breakdown detection method

Environmental conditions during the experiment (temperature, pressure, humidity, if recorded)

[Write your setup description here.]

## 1.2 Measurement Results and Breakdown Characteristics

Report the breakdown voltage Û_d as a peak value in kV. For each AC measurement, calculate the mean field strength, the geometry factor, the utilisation factor and the maximum field strength:

E_mean = Û_d / s        p = (s + r) / r  (equivalent point radius r = 0.5 mm)

η = E_mean / E_max  (for plate-plate the field is homogeneous, so η = 100 % and p is not used; η(p) for point-plate from the Schwaiger diagram in the lecture notes)        E_max = E_mean / η

Table 1.1: AC breakdown voltages of air (Part 1a)

| Geometry | s / mm | Û_d / kV | E_mean / (kV/cm) | p | η / % | E_max / (kV/cm) |
| --- | --- | --- | --- | --- | --- | --- |
| Plate-plate | 10 |  |  | n/a | 100 |  |
| Plate-plate | 20 |  |  | n/a | 100 |  |
| Plate-plate | 30 |  |  | n/a | 100 |  |
| Plate-plate | 40 |  |  | n/a | 100 |  |
| Plate-plate | 50 |  |  | n/a | 100 |  |
| Plate-plate | 60 |  |  | n/a | 100 |  |
| Point-plate | 30 |  |  |  |  |  |
| Point-plate | 40 |  |  |  |  |  |
| Point-plate | 50 |  |  |  |  |  |
| Point-plate | 70 |  |  |  |  |  |
| Point-plate | 100 |  |  |  |  |  |
| Point-plate | 120 |  |  |  |  |  |
| Point-plate | 150 |  |  |  |  |  |

Table 1.2: Pre-breakdown phenomena, point-point, s = 150 mm (Part 1b)

| Stage | Inception voltage / kV | Observation |
| --- | --- | --- |
| Glow onset |  |  |
| Streamer onset |  |  |
| Spark onset (breakdown) |  |  |

Table 1.3: DC breakdown, point-plate, polarity effect (Part 2)

| Polarity | s / mm | Û_d / kV | PD inception / kV | Streamer onset / kV |
| --- | --- | --- | --- | --- |
| Positive point | 30 |  |  |  |
| Positive point | 40 |  |  |  |
| Positive point | 50 |  |  |  |
| Positive point | 70 |  |  |  |
| Positive point | 100 |  |  |  |
| Positive point | 120 |  |  |  |
| Positive point | 150 |  |  |  |
| Negative point | 30 |  |  |  |
| Negative point | 40 |  |  |  |
| Negative point | 50 |  |  |  |
| Negative point | 60 |  |  |  |

Create diagrams of breakdown voltage against electrode spacing. Your diagrams should include:

Four curves: AC plate-plate, AC point-plate, DC point-plate with positive point, DC point-plate with negative point

For each DC polarity, the partial discharge inception voltage as a function of spacing, in the same diagram as its breakdown curve

Axes: breakdown voltage Û_d (kV) on the y-axis and electrode spacing s (mm) on the x-axis

Measured data points with trend lines, and a legend identifying each configuration and polarity

[Insert Figure 1.1: AC breakdown voltage against spacing]

[Insert Figure 1.2: DC breakdown and PD inception voltage against spacing, both polarities]

## 1.3 Analysis: Breakdown Distance, Voltage and Configuration

Analyse and discuss the relationships between breakdown voltage, electrode spacing and electrode configuration. Address the following:

1.	Describe how breakdown voltage varies with electrode spacing for each configuration. Is the relationship linear or non-linear?

2.	Compare plate-plate (uniform field) and point-plate (non-uniform field) breakdown. Use your values of η and E_max to explain the difference.

3.	Explain the physical mechanisms responsible for the observed differences, considering field strength distribution, Townsend ionisation and streamer formation.

4.	Analyse the polarity effect: how does the breakdown voltage differ between positive and negative point configurations, and what are the underlying physical reasons (space charge)?

5.	Relate the pre-breakdown stages in Table 1.2 and the partial discharge inception in Table 1.3 to the breakdown process.

6.	Discuss practical implications for the design of high voltage equipment and insulation coordination in power systems.

[Write your analysis and discussion here.]

# Part 2: Protection Laboratory. Current Transformers and Distance Protection

Maximum 4 pages

## 2.1 Purpose of Current Transformers (CT)

Explain the fundamental purpose and application of current transformers in power system protection. Include:

Primary function: transformation of large primary currents to measurable secondary currents

Safety and isolation: electrical isolation between the high voltage primary circuit and the low voltage secondary measurement and protection circuits

Standardisation: conversion to standard secondary currents (typically 1 A or 5 A)

Application in protection systems: the role of the CT in providing accurate current information to relays

Accuracy requirements: measuring CTs (accuracy class, instrument security factor FS) versus protection CTs (accuracy limit factor), and why accuracy matters for relay operation

[Write your discussion here.]

## 2.2 CT Experimental Setup and Test Purpose

Describe the experimental setup and procedure used for testing the current transformer. Include:

Circuit topology and components for the direct measurement: variable transformer T1, current limiting resistor RB, CT under test, burden ZB

Primary and secondary winding connections (P1/P2, S1/S2)

Measurement instruments (TRMS meters, oscilloscope, calibrated current clamps) and what each one measures

Internal resistance measurement with the Thomson bridge, and the measured burden impedances (Table 2.1)

Definition of the burdens used: rated burden Z_BN, overloading Z_B > Z_BN and underloading Z_B < Z_BN

The purpose of each measurement: direct measurement at rated, over- and underload; indirect measurement of U2 = f(I2), if performed

Table 2.1: Internal resistance of the CT and burden impedances including cabling

| R_i seen from primary / Ω | R_i seen from secondary / Ω | Z_B1 / Ω | Z_B2 / Ω | Z_B3 / Ω |
| --- | --- | --- | --- | --- |

[Write your setup description here.]

## 2.3 CT Performance Analysis. Measurements and Error Calculation

Use the definitions of IEC 61869-2 given in the lab instructions (section 5.1), with K_n the rated transformation ratio (K_n = 1 for the CT tested) and f = 50 Hz:

Current error:            ε_I = (K_n · I_2 − I_1) / I_1 · 100 %

Phase displacement:   δ_I [min] = Δt [μs] · 10⁻⁶ · 360° · f · 60 = 1.08 · Δt [μs]

Composite error:        ε_C = I_d / I_1 · 100 %   (I_d measured directly as the residual current)

Optional cross-check: for sinusoidal currents, ε_C ≈ √(ε_I² + (100 · δ_I [rad])²) with δ_I [rad] = δ_I [min] · π / 10 800. Comment on any deviation from the measured ε_C, for example due to waveform distortion in saturation.

Table 2.2: Direct measurement with rated burden Z_BN = ____ Ω (Table 2 of the lab sheet)

| I_1 / I_1n | I_1 / A | I_2 / A | ε_I / % | I_d / A | ε_C / % | U_2 / V | Δt / μs | δ_I / min |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 5 % |  |  |  |  |  |  |  |  |
| 20 % |  |  |  |  |  |  |  |  |
| 40 % |  |  |  |  |  |  |  |  |
| 60 % |  |  |  |  |  |  |  |  |
| 80 % |  |  |  |  |  |  |  |  |
| 100 % |  |  |  |  |  |  |  |  |
| 120 % |  |  |  |  |  |  |  |  |

Show one complete calculation of ε_I, δ_I and ε_C at 100 % I_1n. Put the measurement tables for overloading and underloading (Tables 3 and 4 of the lab sheet) and, if performed, the indirect measurement (Table 5) in Appendix B.

[Show your sample calculation here.]

Provide the following diagrams and answer the questions:

1.	ε_I = f(I_1) and δ_I = f(I_1) up to 120 % I_1n at rated burden, one diagram each, with the limits for accuracy class 1 drawn in. Are the requirements met?

2.	I_2 = f(I_1) for rated, over- and underload in one diagram. What relationship do you see between burden and measurement error?

3.	ε_C = f(I_1) for the different burdens. Determine the instrument security factor FS at rated burden from the curve and calculate the secondary limiting e.m.f. U_H.

4.	Determine FS_x for the other burdens from the diagram and compare with the values calculated from the formula in the lecture notes.

5.	If the indirect measurement was performed: plot U_2 = f(I_2), determine the saturation voltage U_L and compare it with U_H.

[Insert Figures 2.1 to 2.4 and your answers here.]

## 2.4 Distance Protection. Experimental Setup and Purpose

Describe the experimental setup and purpose of the distance protection tests. Include:

Network model configurations used: radial network type B (SD 34A and KU relay tests), parallel line and ring network (SIPROTEC 7SA511 tests)

Relay types tested (electromechanical SD 34A, KU auto-reclosing relay, digital SIPROTEC 7SA511) and their main characteristics

Circuit topology: how the network model is built, where the relays are located and how current and voltage transformers are connected

Principle of distance protection: how impedance measurement detects a fault and estimates its distance

Zone (stage) settings: the reach of zones 1 to 3 and the time delays used in the lab, and why zone 1 is set to less than 100 % of the line

Test scenarios: 1-, 2- and 3-pole short circuits, faults at the zone 1 boundary, faults with arc, and faults with and without successful arc extinction (auto-reclosing)

[Write your setup description and explanation of zone settings here.]

Table 2.3: Distance protection test results

| No. | Relay | Network model | Fault location | Fault type | Expected zone / time | Measured Z / Ω | Trip time / s | Selective (Y/N) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |

Discuss the results: did each relay trip in the expected zone and time, was the fault cleared selectively, and how did arc resistance and auto-reclosing affect the behaviour?

[Write your discussion here.]

# Part 3: SCADA Laboratory. Power System Operation

Maximum 2 pages

## 3.1 Network Overview and Measurements

Briefly describe the grid training simulator and the network control system (voltage levels, substations, main screens). Report the values you read in exercise 1:

Table 3.1: Readings from the network control system

| Quantity | Value | Unit |
| --- | --- | --- |
| Current network loading |  | MW |
| Current network losses |  | MW |
| Cost of losses |  | EUR/h |
| Coal plant Nordost 400: P |  | MW |
| Coal plant Nordost 400: Q |  | MVAr |
| Line West 400 - Nord 400: loading |  | % |
| Line West 400 - Nord 400: ΔP |  | MW |
| Line West 400 - Nord 400: ΔQ |  | MVAr |
| West 20, branch to Festwiese: P / Q / I |  | MW / MVAr / A |
| West 20, busbar SS1: U1E / U2E / U3E / U12 |  | kV |

## 3.2 Switching Operations

Choose two of the switching exercises you performed (circuit breaker maintenance in Mitte 20, busbar change in UW Ost 20, transformer changeover in West 20). For each one:

Give the switching sequence as a numbered list of operations, in the order you executed them

Show how the five safety rules were applied, and which steps were done centrally (control centre) and which locally

Explain the transfer of disposition authorisation (DA) between the control centre and the local work responsible

Explain how supply interruption was avoided

[Write your two switching sequences here.]

## 3.3 Discussion

1.	Why may a disconnector bridge between busbars exist only temporarily, and why must disconnectors not be operated under load?

2.	Why must the voltage difference be below 300 V before two transformers are switched in parallel? If you performed the parallel transformer exercise, explain the circulating current you observed when the tap positions differed.

[Write your discussion here.]

# Appendix A: Photographs

Attach photographs with a short caption each: electrode configurations and HV setup; CT test setup and measurement equipment; distance relays, settings and network model; simulator screens. Not counted in the page limits.

[Insert photographs here.]

# Appendix B: Raw Measurement Tables

Attach the completed measurement tables from the lab sheets that are not reproduced above, in particular CT Tables 3, 4 and 5. Not counted in the page limits.

[Insert tables here.]